|  | INSTALLATION INSTRUCTIONS FOR SOLID DOUBLEWALL TANK SUMPS Solid (1 joint) Tank Sump Models: B400-D-AB B400-D-AB-MW B400-D-AB-MB B400-D-AB-WT |  |
| --- | --- | --- |

2929 Vail Ave. - Commerce, CA 90040 (323) 888-4133 - FAX: (323) 888-4123 www.SBravo.com

ii-B400-DW-SD-10A

ATTENTION:

This S. Bravo Systems, Inc,  B-409 DoubleWall  Sump with Bottom  MUST be installed by a Bravo Certified Installer. Get Certified at www.sbravo.com/cert.

DO NOT fill this DoubleWall system with brine or saline solution. Doing so will void the warranty. Use ONLY Bravo-supplied Interstitial Fluid. The warranty is also void in there is any indication of modification, abuse, negligence,  or improper installation.

Pay strict attention to the directions and warnings indicated on the product, or contained in these instructions, including those found on OTHER manufacturers directions and warnings, including, but not limited to, equipment and products used in the installation and operation of Bravo Systems Products.

Bravo recommends you read this entire manual before beginning installation. If you can't read this manual, ask your supervisor to read it to you or have someone who can read it to you.

Warranty is void if there is any evidence of modification, abuse, negligence or improper installation. For assistance please call Bravo for technical support at (800) 28-BRAVO.

Outside the U.S.A. please call (323) 888-4133.

SAFETY FIRST!

S. Bravo Systems, Inc. urges you to strictly abide by the normal safety procedures and precautions followed by your company. Please follow the mandates and compliances decreed by OSHA, local, State and federal regulations regarding the use of this product.

WARRANTY

All containment systems sold by S. Bravo Systems, Inc. are warranted to be free from defects in material and workmanship for a period of one year from date of purchase. This warranty will be limited to the repair and replacement of Bravo parts only and will exclude all claims for labor or consequential damage. No other express warranties given and no affirmation of S. Bravo Systems, Inc., or its agents and/or representatives, by words or action, will constitute a warranty. IT IS EXPRESSLY AGREED THAT THIS WARRANTY WILL BE IN LIEU OF ALL WARRANTIES OF FITNESS AND IN LIEU OF THE WARRANTY OF MERCHANTABILITY. This warranty is void if there is any evidence of modification, abuse, negligence, or improper installation. If any fittings or components, other than S. Bravo Systems approved fittings or components, are used in conjunction with any S. Bravo Systems product, the warranty

pertaining to these products is immediately void.

IN CALIFORNIA:

The installer must observe and comply with the volume containment requirements found in the California Code of Regulations CCR Title 23, Article 3, section 2631(d)(1). The regulation can be found at: //www.swrcb.ca.gov/water_issues/programs/ust/regulatory/

under California Regulations > UST Regulations

FOR TALL BASE/COLLAR ONLY BEFORE INSTALLING PENETRATION FITTINGS SUMP ‘TOP HAT’ BODY ARE HOLDING VACUUM. If the gauge is Below 12 inches of mercury (Hg/Vacuum) you must hold the Sump at 20 INCHES OF MERCURY for no less than 24 hours.

The installer of this equipment is required to visually check the vacuum gauge on each and Bravo Systems DoubleWall product and record those findings on the FAX report Vacuum Level, Name Of Observer, and Date for every DoubleWall Sump.

THE WARRANTY IS VOID IF ANY OF THE FOLLOWING OCCUR:

A failure to comply with the Required Written Report Guidelines as stated above.

Double Wall Products are DOUBLE-STACKED, stored or shipped in a negligent way.

Any packaging or wrapping materials are removed before the item reaches It’s destination.

Double Wall Sump Products, Failure to call Bravo Systems If Vacuum level on product is less than 12” HG (Vacuum) (323) 888-4133, refer to sump for further details.

Double Wall Sump Products are tested per the SB989 Testing procedures. The interior of these sumps must NOT be filled with liquid to any level

Double Wall Sumps are filled with an unapproved interstitial fluid, or if adhesives or sealants are used that are not Bravo-approved.

If there is any indication or suspected damage, you must mark the freight paperwork “Suspect Freight Damage” as directed by your Contractor Warranty sheet.

DO NOT PLACE FIBERGLASS PIPING SUMP(S) ON

THE COLLAR AND ATTEMPT TO SEAL THE JOINT(S).

READ STEP-BY-STEP INSTRUCTIONS FIRST.

CAUTION:

BEFORE PENETRATING FIBERGLASS WALLS

ENSURE THAT EACH DOUBLE WALL FIBERGLASS SUMP IS HOLDING VACUUM

DO NOT drop the sump body or tank collar on the ground or roll it to its

destination or forcefully dry fit the sump body on the tank collar.

Secure and protect sumps from high wind conditions.

The installer of this equipment is REQUIRED to visually check the Vacuum gauge on each and every Bravo Systems Double Wall product and write on the FAX report Vacuum level, name of observer, and date for every DoubleWall Sump.

WARRANTY IS VOID IF ANY OF THE FOLLOWING OCCUR

There is a failure to comply with the Required written report guidelines as stated above.

Double Wall Products are DOUBLE-STACKED, stored or shipped in a negligent way.

Any packaging or wrapping materials are removed before the item reaches Its destination.

Double Wall Sump Products, Failure to call Bravo Systems If Vacuum level on product is less than 12” HG (Vacuum) (323) 888-4133, refer to sump for further details.

Double Wall Sump Products are tested per the SB989 Testing procedures. The interior of these sumps must NOT be filled with liquid to any level.

Double Wall Sumps are filled with an unapproved interstitial fluid, or if adhesives or sealants are used that are not Bravo-approved

Double Wall Sumps are filled with an unapproved interstitial fluid, or if non-Bravo-approved adhesives or sealants are used.

If there is any indication or suspicion of damage, the installer must mark the freight paperwork  “Suspect Freight Damage” as directed by your Contractor Warranty sheet.

EQUIPMENT DRY-FIT

- BEFORE INSTALLING PENETRATION FITTINGS

- BEFORE CUTTING OPEN SUMP INTERSTICE

DRY-FIT YOUR SUMP PIECES AND INTERNAL EQUIPMENT.

PLAN YOUR INSTALLATION AND MAKE SURE EVERYTHING FITS, AND WILL FIT

LATER DURING INSTALLATION.

After your Primary tank(s) have arrived, ensure the tank collar, joint of the tank collar, and piping sump, is clean of debris. Also visually inspect the parts provided by Bravo Systems for transit damage and/or missing parts. Continue to keep the

Sweep away any gravel, dirt or debris around the OUTSIDE where the tank collar meets the tank so that you will be able to see possible leaks.

Install Penetration Fittings per their respective Installation Instructions. You must NOT disturb the penetration fittings while the sealant/adhesive is drying. Allow for the maximum cure time as recommended by the manufacturer of the fittings before pressurizing & soaping to test for leaks.

IMPORTANT: DO NOT FILL DOUBLE WALL PENETRATION FITTINGS WITH FOREIGN MATERIALS, SEALANTS or ADHESIVES.

If the Sump was holding Vacuum as described above, any leaks may be credited to the Installation of the Penetration Fittings. Install stub / dummy pipe in all the penetration fittings and use the factory provided Vacuum/Pressure gauge to pressure the sump to 4 PSI and soap ALL fittings, inside and outside. If foaming leaks are found, repair or reinstall per manuf. Inst ructions.

IMPORTANT: MAKE SURE TO FILL OUT AND FAX YOUR WARRANTY FORMS ATTACHED TO EACH DOUBLE WALL FIBERGLASS SUMP. FAX TO 323-888-4133 TO ACTIVATE YOUR WARRANTY.

PROCEED TO THE NEXT STEP TO BEGIN THE CUTTING AND GRINDING PROCESS TO PREPARE FOR FIBERGLASSING THE BODY OF THE SUMP TO THE BASE/TANK COLLAR.

INCLUDED  COMPONENTS

Provided

1 SLURRY KIT PER SPLIT SUMP (2 JOINTS) inside/outside. See Figure 1.

2.5 Gal of Resin.

1 Qt. of Paste.

Resin Catalyst.

Paste Catalyst.

Mixing Buckets.

4 Pairs Nitrile Gloves.

One 90’ Roll of Fiberglass Mat.

An extra 30’ roll of fiberglass mat.

Four 4-1/2” Roller Covers.

Two sheets of 60-grit Sandpaper.

Four Sheets Blue Shop Towels.

Manometer Kit. Interstitial fluid.

Figure 1: Resin Kit

Keep sumps and slurry shaded

and out of direct sunlight

CRITICAL

INFORMATION :

1 TOOL KIT (per site)  See Figure 2.

One 4” Paint Roller,

Figure 2: Tool Kit

One Metal Paste Mixer,

One Paint Stirring Stick,

One 4” Putty Knife,

One Metal Chamfer Roller,

One 5 quart mixing bucket.

One 250’ by 1” Roll of

- Masking tape per 2 Sumps.

MSDS for materials.

1 MANOMETER KIT (PER SUMP) HYDROSTATIC ONLY!!

Interstitial fluid

Standard Manometer

Manometer Bracket

Factory-Installed

Nylon tubing

w/20”Hg Vacuum on interstice

w/Combination Pressure/Vacuum Gauge

TABLE OF CONTENTS

1.	PREPARING THE COLLAR AND TANK SUMP BASE	10

1.1.	Step by Step Overview	10

1.2.	Abrade and Trim	11

2.	JOINING THE BASE TO TANK COLLAR	11

3.	FIBERGLASSING THE BODY TO TANK COLLAR.	15

4.	TESTING THE BASE/COLLAR INSTALL	18

5.	TESTING THE DBLWALL SUMP INSTALL	19

5.1.	Leaks Are Detected	19

6.	MANDATORY AIR INTEGRITY TEST	20

6.1.	Maximum Pressure	20

6.2.	IF ANY LEAKS ARE FOUND	21

7.	VACUUM / HYDROSTATIC FILLING	21

7.1.	Field Air Integrity Inspection Test:	22

F.1 -	After Passing Field Air Integrity Test	22

8.	ADVANCED LEAK DETECTION PROCEDURE	24

8.1.	ALDP In Action Diagram	25

9.	ATTACHING THE MANOMETER	26

9.1.	Hydrostatic Field Integrity Test	27

10.	CONCRETE AND BACKFILL GUIDELINES.	28

LIST OF FIGURES

Figure 1: Resin Kit	6

Figure 2: Tool Kit	6

Figure 3: Top of the Base/Tank Collar	11

Figure 4: Abrade Tank Collar	11

Figure 5: Tank Sump Base Is Square	11

Figure 6: Tank Sump Centered.	12

Figure 7: Apply Masking Tape	13

Figure 8: Apply Paste Carefully	14

Figure 9: Carefull Application	14

Figure 10: A Neat and Careful Job	14

Figure 11: Inside Joint Applied	14

Figure 12: Apply Resin Generously	16

Figure 13: Fully Saturate Fiberglass	16

Figure 14: Stagger the Layers	16

Figure 15: Chamfer Roll To Run Out Air	16

Figure 16: Outside Joint Overlapped	17

Figure 18: Smooth and Even	17

Figure 19: Inside Joint	17

Figure 20: Barrel Roller	17

Figure 21: Chamfer Roller	17

Figure 17: Chamfer Rolled	17

Figure 22: Sand Smooth	18

Figure 23: Apply Resin	18

Figure 24: 4 PSI	20

Figure 25: Field Air Integrity	22

Figure 26: Liquid Funnel	23

Figure 27: Ball Valve	23

Figure 28: Pull Vacuum	24

Figure 29: Leak Detection	25

Figure 30: Connect To Primary Manometer	27

Figure 31: Tank Shoulder	29

# PREPARING THE COLLAR AND TANK SUMP BASE

Always wear gloves when handling piping sump components, and always wear eye protection when grinding, cutting, or applying resin to the components.

## Step by Step Overview

Determine overall Tank Sump height based on the plans for grade level. You will then perform the following actions in order:

NOTE: All steps to Abrade are inside and outside the Sump

- If you have a Base/Collar (tall) Install your penetration fittings (Page 5)

- If you have a short collar, skip to Number 3.

- If you have a Base/Collar (tall) Cut the minimum 2” from top of the base/Collar

- Abrade 4” down from top of Collar, dust off, keep clean

- Cut the bottom of the Body to attain the necessary overall height required to reach Grade specifications

- Abrade 4” up from bottom of Body, dust off, keep clean

- Carefully join the Body to Collar, Tape joint inside & out

- Mix Paste with Catalyst and apply OVER the taped joint to smooth out wall transition in case of difference in Diameter

- Fiberglass the Body to the Collar and let cure, lightly sand, and flow-coat the joint, inside & outside, let cure

- Test the interstice: Pressure & Soap the Fiberglass job

- If you have a Short Collar, Install your penetration fittings

- After fitting installation, pressure & soap the fittings

- Field Air Integrity Test: 4 PSI on interstice and wait one hour before beginning test. Mark time, monitor for one hour

- Hydrostatic Filling and Advanced Leak Detection Procedure

- Field Integrity Test: Mark liquid level and monitor one hour

- Protect Tank Sump Reducer and Backfill

## Abrade and Trim

- Trim the Top of piping sump Base/Collar 2” from TOP EDGE only using a carbide tipped blade or masonry saw. Material must be cut square with a 1/4" +/- tolerance to open the double wall space 360° around sump.. See Figure 3.

Trim the Bottom of piping sump BODY the necessary amount to reach grade from BOTTOM EDGE only using a carbide tipped blade or masonry saw as shown in Figure 3.  Material must be cut square with a 1/4" +/- tolerance to open the double wall space 360° around sump.

Abrade with air-driven sander 4 inches down from top edge of Tank Collar - Inside and Outside - until fiberglass surface can be seen clearly, as shown in Figure x. Dust off with shop brush and keep clean.

| Figure 3: Top of the Base/Tank Collar | Figure 4: Abrade Tank Collar |
| --- | --- |

# JOINING THE BASE TO TANK COLLAR

Fit the clean Tank Sump BASE on the tank collar and ensure it fits squarely in place

(Fig. B.1.1 - B.1.2). Ensure walls are fully abraded down to the glass fibers.

Figure 5: Tank Sump Base Is Square

Ensure Tank Sump is centered, plumb and stationary. Alignment may be critical for the fill sump.

Figure 6: Tank Sump Centered.

You must remove the Schrader Cap from the Gauge assembly and screw on the SVA-BARB (Schrader Valve Adapter w/Barb) (see below) on all DoubleWall products that will be fiberglassed.

IMPORTANT: While Joining sumps, and installing fittings, keep the SVA-BARB in place. This will relieve pressure on the Interstice while the sumps expand and contract with temperature changes.

| Gauge Assembly | CAP | SVA-BARB |
| --- | --- | --- |

Apply provided masking tape to the joint edge overlapping the ends securely. Tape the inside

and outside joint of the transition. Use extra if necessary. See Figure x.

Figure 7: Apply Masking Tape

Gather together all PC Slurry materials and tools. Ensure surfaces inside and outside of the

joint transition and surrounding walls are free of debris, clean, and COMPLETELY DRY! .

NOTICE: THE PASTE CATALYST BOTTLE HAS A RED STICKER

FOR SUMMER: 1/2 bottle per 1/4 Gallon of putty.

FOR WINTER: 14 Oz per 7/8” Gallon of PC Slurry.

WARNING:  Wear protective goggles, mask and gloves when mixing and applying resin or paste.

Apply the mixed paste material to the sump joint, over the applied tape and over its edges to meet the fiberglass wall. Be careful.  Do not be sloppy. The more paste applied past the tape the more work it is to remove it later.

| Figure 8: Apply Paste Carefully | Figure 9: Carefull Application | Figure 10: A Neat and Careful Job |
| --- | --- | --- |

Wait for the paste to fully cure. PIPING SUMP MUST NOT BE DISTURBED

DURING THIS TIME TO AVOID MISALIGNMENT.

After exterior joint(s) have fully cured, mix paste and smoothly apply to the inside joint of the

piping sump, over the tape and its edges, as shown in Figure 10. Visually inspect the Joints that the paste has been applied to and look for gaps or delaminating. Ventilate sump accordingly, if mandated by local or federal regulations.

Figure 11: Inside Joint Applied

After Paste has fully cured, grind down all previously abraded areas (Fig. B.7.3) and lightly touch up pasted area with additional paste as needed.Dust off abraded areas.

# FIBERGLASSING THE BODY TO TANK COLLAR.

ENSURE THAT THE SUMPS ARE COMPLETELY DRY,

FREE OF DEBRIS, ICE AND/OR SNOW.

DO NOT HANDLE ANY FIBERGLASS SUMP WITH YOUR BARE HANDS.

C.1 - Pre-cut several dozen pieces of 6” wide fiberglass mat to lengths of 20-24”. You will need four (4) layers of these fiberglass mat strips for the INSIDE and OUTSIDE joints of each piping sump.

C.2 - Use the mix stick to mix the resin and catalyst thoroughly.

For SUMMER -  1/4 bottle per 1/4 Gallon of resin.

For WINTER - 1/2 bottle per 1/4 Gallon of resin.

C.3 - Use paint roller to apply resin generously to a smooth surface. Spread the resin so it ‘wets out’ an area larger than the strip of fiberglass mat as shown in Figure 11.

C.4 - Apply one layer of fiberglass mat to the resin. Use the paint roller to add more resin to fully saturate it. See Figure 12.

C.5 - Lay down another strip of fiberglass mat, staggering the new layer ONE INCH. This means to offset the next fiberglass strip horizontally (lengthwise) 1” to the right. Roll more resin into the new strip to saturate it as shown in Figure 13.

C.6 - Repeat Step C.5, offsetting another strip of fiberglass mat and using the paint

roller to add more resin to it until it is fully saturated. See Figure 14.

C.7 - Repeat once more Step C.5 for a total of 4 layers.

C.8 - Use a Chamfer roller to completely roll over the pre-soaked fiberglass strip while it is on the cardboard, horizontally and vertically, to run out any air bubbles as shown in Figure 14.

C.9 - Apply the fiberglass patch to the OUTSIDE JOINT of the piping sump centered on the joint. Apply saturated fiberglass strips all the way around the piping sump, EVENLY OVERLAPPING EACH 2 FOOT STRIP 3 INCHES OVER THE LAST. See Figure 15.

| Figure 12: Apply Resin Generously | Layer 1 Figure 13: Fully Saturate Fiberglass |
| --- | --- |
| Layer 2 Figure 14: Stagger the Layers | Chamfer Roller Layer 3 Figure 15: Chamfer Roll To Run Out Air |

Apply fiberglass strips horizontally (ACROSS the piping sump, not up and down.)

The completed glass job should be air-free, seamless and ripple-free as shown in Figure 17.  Roll over the fiberglass mat many times with a Chamfer roller (provided) on the OUTSIDE JOINT to make sure it is cleanly adhered to the fiberglass piping sump walls. Run the roller up and down to force any air out from under the fiberglass strip, as shown in Figure 16.

| Figure 16: Outside Joint Overlapped | Figure 17: Chamfer Rolled | Figure 18: Smooth and Even |
| --- | --- | --- |

C.10 - Repeat Steps C.4 to C.9 and apply fiberglass strips to the INSIDE JOINT of the piping sump. See Figure 18. For the INSIDE fiberglass strips use a Barrel roller to apply the strips to the curved surface as shown in Figure 19.

C.11 - Use a Chamfer roller to carefully roll over the applied fiberglass strips to run out any air bubbles. See Figure 21

| Figure 19: Inside Joint | Figure 20: Barrel Roller | Figure 21: Chamfer Roller |
| --- | --- | --- |

C.12 - Allow at least 4 hours at 75 Degrees to cure. During this time, continue on to other sumps.

C.13 - When all fiberglass applications have cured, sand them down lightly with air-sander or roughly with coarse 40 - 60 grit sandpaper all the way around the piping sump to knock down all excess fiberglass ‘hair’ and material. See Figure 21.

C.14 - Mix resin and apply with paint roller, completely covering the fiberglass material all the way around the piping sumps. Roll resin generously with paint roller. DO NOT USE PUTTY KNIFE or other scraping tool. The resin needs to be applied generously and evenly as shown in Figure 22.

| Figure 22: Sand Smooth | Figure 23: Apply Resin |
| --- | --- |

C.15 - Now install any/all equipment in the piping sump(s) that will not interfere with iberglassing the top portion of the sump. Install all necessary equipment per local code & regulations. Follow installation instructions / recommendations / warnings provided by equipment manufacturer(s).

# TESTING THE BASE/COLLAR INSTALL

Remove & save the SVA-BARB from the Gauge Assembly Schrader Valve (Refer to Step B.3)

D.1 - Sweep away any gravel, dirt or debris around the OUTSIDE of the piping sump, where 	  	the tank collar meets the tank so that you will be able to see possible leaks.

D.2 - Pressurize the interstice to 4 PSI and soap the fiberglass joint, inside and outside. If 	 	sump is holding, keep record.

D.3 - Leaks Detected

Look at edges and corners for pinhole leaks. For large leaks, consult factory.

- Locate leak point(s) and mark with marker so you can locate it / monitor it.

Repair or reinstall doublewall penetration fittings according to your doublewall penetration fitting manufacturers’ Installation / Maintenance Instructions.

Abrade a 2” diameter area centered on the leak point until natural resin/fiberglass material can be seen. Dust with shop brush or compressed air and do not use shop towels or acetone on the abraded area(s). Then apply a 3-layer strip of 2” x 2” resin-saturated fiberglass mat squarely on the abraded area.

Roll out any air bubbles with chamfer roller. Let cure. After cure, knock down fiberglass hairs, and apply another flow coat of resin only (Step C.14). Apply any extra resin to repaired leak point(s) while still wet.

Let cure for a minimum of 4 hours @ or above 75° F.

ALLOW ANY REPAIRS TO FULLY CURE BEFORE TESTING SUMP AGAIN

DO NOT FILL DOUBLE WALL PENETRATION FITTINGS WITH FOREIGN MATERIALS

D.4 - When the Fiberglass installation passes and is holding integrity, Install all your Double Wall Penetration Fittings per their respective Installation Instructions. Re-Install the SVA-BARB to the schrader valves. Do NOT install fittings on joints.

IMPORTANT: THE SUMP WALLS MUST ABRADED FLAT PER THE T-FS-SAND-KIT INSTALLATION INSTRUCTIONS

IMPORTANT: DO NOT INSTALL PENETRATION FITTINGS ON OR NEAR FIBERGLASSED JOINTS. CONSULT BRAVO.

D.5 - After the Fittings have been installed and the sealant/adhesive has fully cured, pressure/soap test all fittings at 4 PSI.

NOTE: Vulkem Sealant, used with Bravo Systems Flexible Penetration Fittings,

must cure overnight.

D.6 - When the Penetration Fitting installation has been successfully tested and is holding integrity, the installation of pipe lines may commence.

# TESTING THE DBLWALL SUMP INSTALL

Remove & save the SVA-BARB from the Gauge Assembly Schrader Valve (Refer to Step B.3)

Sweep away any gravel, dirt or debris around the OUTSIDE of the piping sump, where the tank collar meets the tank so that you will be able to see possible leaks.

Pressurize the interstice to 4 PSI and soap the fiberglass joint, inside and outside. If sump is holding, keep record.

## Leaks Are Detected

Examine edges and corners for pinhole leaks. For large leaks, consult Bravo.

A: Locate leak point(s) and mark with marker so you can locate and monitor it.

NOTE:  If V-Pour Channel or large sump leaks, please contact Bravo at (323) 888-4133

B:  Repair or reinstall doublewall penetration fittings according to your doublewall penetration  fitting manufacturers’ Installation / Maintenance Instructions.

C:	Sump pin hole leaks on body of sump Abrade a 3” diameter area centered on the leak point until natural resin/fiberglass material can be seen. Dust with shop rush or compressed air and do not use shop towels or acetone on the braded area(s). Then apply a 4-layer strip of 6” x 6” resin-saturated fiberglass mat squarely on the abraded area.

D:	Fiberglass repairs Roll out any air bubbles with chamfer roller. Let cure.

E:	After cure, knock down fiberglass hairs, and apply another flow coat of resin only. Apply any extra resin to repaired leak point(s) while still wet. Let cure for a minimum of four (4) hours at or above 75° F.

ALLOW ANY REPAIRS TO FULLY CURE BEFORE TESTING SUMP AGAIN. DO NOT FILL DOUBLE WALL PENETRATION FITTINGS WITH FOREIGN MATERIAL

- D-4.	When the Fiberglass installation passes and is holding integrity, Install all your Double Wall Penetration Fittings per their respective Installation Instructions. Re-Install the SVA-BARB to the Schrader valves. Do NOT install fittings on joints.

THE INSTALLER MUST ABRADE THE SUMP WALLS FLAT PER THE T-FS-SAND-KIT INSTALLATION INSTRUCTIONS. DO NOT INSTALL PENETRATION FITTINGS ON OR NEAR FIBERGLASSED JOINTS.

CONSULT BRAVO.

D.5	After the Fittings have been installed and the sealant/adhesive has fully cured, pressure/soap test all fittings at 4 PSI.

D.6	When the Penetration Fitting installation passes and is holding integrity, pipeline installation may commence.

# MANDATORY AIR INTEGRITY TEST

## Maximum Pressure

Use test assembly and pressure sump to no more than four (4) PSI. Close off with ball valve and resume other work. Allow one (1) hour before recording pressure. 
See Figure 23.

Figure 24: 4 PSI

| NOTICE: BRAVO QUALITY STANDARD | FIELD AIR INTEGRITY INSPECTION TEST : Hold pressure for a minimum of one (1) hour for a Field Integrity Inspection Test. The Tank Sump PASSES the integrity test if the Sump shows NO signs of continuous pressure loss. |
| --- | --- |

IF TEST PASSES: Continue on to the Hydrostatic Fill & Integrity Test

## IF ANY LEAKS ARE FOUND

- Examine edges and corners for pinhole leaks. For large leaks, consult factory.

- Locate leak point(s) and mark with marker so you can find it again it.

- Repair or reinstall doublewall penetration fittings according to your doublewall penetration fitting manufacturers’ Installation / Maintenance Instructions.

- Abrade a 2” diameter area centered on the leak point until natural resin/fiberglass material can be seen. Dust with shop brush or compressed air. DO NOT use shop towels or acetone on the abraded area(s). Then apply a 3-layer strip of 2” x 2” resin-saturated fiberglass mat squarely on the abraded area. Roll out any air bubbles with the chamfer roller. Let cure.

- After cure, knock down fiberglass hairs, and apply another flow coat of resin only. Apply any extra resin to repaired leak point(s) while still wet.

- Let cure for a minimum of four (4) hours at or above 75° F.

FOR HYDROSTATIC MONITORING - PROCEED TO SECTION 3.

FOR CONTINUOUS VACUUM MONITORING - The B409 DoubleWall Solid Sump w/Bottom cannot exceed 16” of Mercury. (Vacuum) Follow your vacuum system manufacturer’s installation instructions to install, seal, and monitor the doublewall system with vacuum.

Connect the SVA-BARB to your factory-installed gauge

for vacuum monitoring

| CAUTION: | Ensure that the fittings used in the Vacuum Monitor System can withstand the amount of Vacuum your Monitoring System will generate. |
| --- | --- |

# VACUUM / HYDROSTATIC FILLING

## Field Air Integrity Inspection Test:

- Failure to conduct a field air  integrity inspection test  that holds pressure for a minimum of one (1) hour will voice the warranty. After passing the pressure test, it is highly recommended that the four (4) PSI  be maintained for as long as possible or until time for the backfill.

BE AWARE: Your product warranty will be revoked if you Choose to skip the air integrity test outlined in your Copy of your product installation instructions. The pressure test MUST be  completed prior to hydrostatic filling of the sumps.

- The Bravo Double Wall products ship from the factory with a combination gauge factory- installed and held under 20” of mercury / vacuum.

## F.1 -	After Passing Field Air Integrity Test

After the test is conducted per the Installation Instructions, and there are no signs of leaks, cut the permanently affixed pipe plug from the tubing connected to the side wall. See Figure 24. This is NOT the tubing with the gauge connected to it.

F.2 - Connect the barb and ball-valve assembly. (sold separately)  A 36” length of clear tubing is factory installed to the barb-and-ball-valve assembly.

Connect the Assembly to the tubing

Cut the plug end

off the tubing

Barb and Ball Valve Assembly

Figure 25: Field Air Integrity

After the penetration fittings have been installed, the vacuum has been lost. Pressure/soap tests should have been conducted prior to filling the sumps with liquid.. Close off the ball valve and prepare the Venturi Vacuum Generator and air supply to be used to fill Sump with liquid

F.3 - Prime the open ended 36” length of clear tubing with provided Interstitial Fluid. part # IMF-1 GAL Use a liquid funnel. See Figures 25 and 26.

| Figure 26: Liquid Funnel | Figure 27: Ball Valve |
| --- | --- |

CAUTION: Filling Bravo Systems Double Wall Products with brine (saline) solution will void the product warranty. Use only Bravo-Supplied Interstitial Fluid, part # IMF-1GAL.

After liquid fill, conduct the Advanced Leak Detection Procedure detailed in Section 8. Cut the ball valve assembly from its tubing and connect open end of tubing to Primary manometer, detailed in Sections 5. Also unthread the Gauge Assembly  and use provided PVC threaded plug to close off the open test port fitting.

F.4 - After filling the tubing all the way to the ball valve, insert open end into the liquid source. (5 gallon bucket filled with fluid is recommended.) See Figure 27.

F.5 -  When ready, pull vacuum using the Venturi Vacuum Assembly (sold separately) to 20 Inches of mercury. Then SLOWLY open ball valve and allow Interstitial fluid to flow freely into the system at a rate of about 2 gallons a minute. See Figure 12.

IMPORTANT:  Open the ball valve SLOWLY.

Stop Pulling vacuum when the liquid is 2-3 inches from the very top of the interstitial space / test port. This is easily visible while filling the doublewall product.

Bucket

Barb & Ball

Valve Assembly

Figure 28: Pull Vacuum

# ADVANCED LEAK DETECTION PROCEDURE

A Bravo Systems Exclusive Detection Method

G.1 - Clear debris from the top open area of the DoubleWall Product and ensure that the interior walls are clean of debris and visible.

G.2 - Apply Vacuum to the sealed interstitial space with the Venturi Vacuum Assembly, and generate 20”-30” of vacuum for a MINIMUM of five (5) minutes.

CAUTION: Check with your equipment manufacturers installation manuals for installation guidelines and/or equipment limits regarding vacuum and pressure levels.

G.3 - As stated in the Instructions, the liquid level is deliberately not filled to the very top

of the interstitial space. This pocket of air is necessary to visually check the topmost level of liquid all the way around the Sump for indication of a leak.

G.4 - Visually inspect the interior walls for signs of trailing (very small) bubbles floating to the top of the liquid level within the interstitial space.

NOTE: These air bubbles are visible within the vertical and horizontal channels of the walls. For Tank Sumps look below the reducer.

NOTE: On the top hat reducer of a Tank Sump, any bubbles will burp consistently.

CRITICAL:   Pay close and special attention to field-installed penetration fittings and FRP joints on tank sumps. These are common leak points.

CAUTION:  Even though Bravo DoubleWall product corners and edges are thicker than the rest of the Containment sump, These areas are  the most susceptible top physical damage by Installation Contractors. Be extremely careful with these   DoubleWall products while storing, moving, transporting and Installing these critical environmental components. 9 ii-B409-DW-12A. Even though Bravo DoubleWall product corners and edges are thicker than the rest of the Containment sump, You would do well to be extremely careful with these DoubleWall products while storing, moving, transporting and installing these critical environmental components.

## ALDP In Action Diagram

Figure X shows a leak while a strong vacuum is pulled on the Interstitial space, forcing tiny air bubbles into the interstitial space to travel upwards. These streams of bubbles are easily spotted and can be traced down to its leak point or area. See Figure 28.

Figure 29: Leak Detection

CRITICAL: Pay close and special attention to field-installed penetration fittings and FRP joints on tank sumps. These are common leak points, as are the corners and edges of the Containment Sump

CAUTION: Even though Bravo DoubleWall product corners and edges are thicker than the rest of the Containment sump, These areas receive the most susceptible to physical damage by Installing Contractors. You would do well to be extremely careful with these DoubleWall products while storing, moving, transporting and Installing these critical environmental components.

# ATTACHING THE MANOMETER

H.1 - After the ALDP test, the interstice should still be holding vacuum. Maintain 20” of  Vacuum and slowly open the ball valve to let fluid into the interstice until it exits the venturi assembly. Visually check whether the fluid level reaches the top of the interstitial space.

H.2 - Cut the barb & ball valve assembly free by cutting the tubing just below it and connect the open end of tubing to the bottom of the primary Manometer as shown in Figure 14.

- H.3 - Remove the Barb, Tubing & Combination gauge assembly from the test port fitting on the side of the sump. Install a threaded pipe plug into the open test port fitting and adjust Primary manometer bracket so the manometer is in a position clear of the sump cover.

Remove entire gauge assembly by backing off threaded barb fitting.

P-Traps OK since vacuum fill method leaves no room for air

Install PVC Plug

Connect Tubing to Primary Manometer

Cut off barb and ball valve assembly

Figure 30: Connect To Primary Manometer

- H.4 - It's normal for some interstitial fluid to be lost while connecting the tubing to the primary manometer. Replace lost fluid by topping off manometer with interstitial fluid until the liquid level reaches just 2 inches below the top of manometer.

## Hydrostatic Field Integrity Test

Mark the date and time of test and manometer level. Allow 1 hour then check for a change in level. No change in level or visible leaking means box passes test.

- H.5 - If interstitial test fluid changes its level more than 1/4”, visually look for any signs of leaking around fittings both interior and exterior to sump. Pay special attention to field installed fittings.

- H.6 - If interstitial monitoring is required, install a California Listed Hydrostatic Sensor (LG-113) using the sensor manufacturer’s fitting. Run sensor cable through the cap assembly. See Figure x.  Level sensor should be set to bottom of manometer. Follow your leak detector manufacturer’s installation instructions. Cover the manometer with cap and fasten with wire and lead crimp seal.

# CONCRETE AND BACKFILL GUIDELINES.

To ensure that no immediate or future damage is done to your Bravo Tank Sump Reducer components, make sure that your manhole skirt DOES NOT TOUCH OR REST ON THE TANK SUMP SHOULDER. The Manhole Skirt should be kept at minimum of 4” away from the tank sump shoulder. Follow the manhole manufacturer's instructions for installing the manhole. Also follow other details provided by tank and/or engineering firm for tank driveway pad installation. See Figure 15.

Backfill your pea gravel around the sump maintaining a minimum of 1’ foot all the way around (if your site backfill is not entirely pea gravel) and 4” minimum distance from the top edge of sump reducer.

With pea gravel in place, use a plastic sheet of a minimum three (3) mil to cover the surface of the pea gravel for at least  two (2) feet away from the sump reducer wall.

Secure this plastic barrier to the EXTERIOR OF THE MANHOLE SKIRT using duct tape. This prevents concrete from seeping too far down into the pea gravel.

Figure 31: Tank Shoulder